Solution to redmine 5112 sRpN5 Ed2Amd1 TP1.1 November 16, 2021

(Previous proposal November 1, 2021 was words “reserves and”, new is “reserves then”)

Update step 8 to first reserve and then configure the URCB to achieve the positive respond:

|  |  |  |
| --- | --- | --- |
| **sRpN5** | **Exclusive use of URCB** | [ ]  Passed[ ]  Failed[ ]  Inconclusive |
| IEC 61850-7-2 Subclause 17.2.1IEC 61850-8-1 Subclause 17.2PIXIT: As2 |
| Expected result2. DUT sends SetURCBValues response- with data access error = temporarily-unavailable4. DUT sends SetURCBValues response+8. DUT sends SetURCBValues response+10. DUT sends SetURCBValues response+11. DUT sends SetURCBValues response- with data access error = temporarily-unavailable13. DUT sends a GetURCBValues response+, the parameter Resv = False14. DUT sends SetURCBValues response+15. DUT sends SetURCBValues response+ |
| Test description1. Client1 reserves an available URCB2. Client2 reserves and configures the same URCB by requesting SetURCBValues with one of the following dynamic (“dyn”) attributes Resv, RptID, DatSet, OptFlds, BufTm, TrgOps, IntgPd3. Client1 resets the reservation of the URCB4. Client2 reserves and configures the URCB 5. Client2 resets the reservation of the URCB6. Client1 reserves the URCB7. Client1 aborts and re-establishes the association 8. Client1 reserves then configures the URCB9. Client1 resets the reservation of the URCB10. Client1 reserves the URCB11. Client2 requests SetURCBValues of a “dyn” attribute12. Disable the TCP communication between Client1 and the DUT. E.g. disconnect the physical link, between two Ethernet switches (preventing Ethernet hardware error detection at both client and server), some seconds longer than the lost connection detection timeout specified in the PIXIT and then enable TCP communication. E.g. connect the physical link13. Client2 requests GetURCBValues14. Client2 reserves the URCB15. Client2 requests SetURCBValues of a “dyn” attribute |
| CommentStep 12 – Tested with a lost detection timeout of …. Seconds. |