|  |  |  |
| --- | --- | --- |
| **sSBOes8** | **Operate with different value then the SelectWithValue of a SBOes control object** | Passed  Failed  Inconclusive |
| IEC 61850-7-2 Table 54  IEC 61850-8-1 Subclause 20.6, 20.7 and 20.8 | | |
| Expected result  1. DUT responds with SelectWithValue response+  2. DUT responds with Operate response- with AddCause “Inconsistent-parameters”, or only when Operate.test=T with  AddCause either “Blocked-by-mode" or “Inconsistent-parameters”  3. The control object will return to the unselected state: stSeld=F or SelectWithValue response+ or Operate response‐ with AddCause “Object‐not‐selected” | | |
| Test description   1. Client sends correct SelectWithValue request of an unselected SBOes object with it’s logical node Beh=on 2. Client sends Operate request of the selected object changing one of the following attributes to another value than the SelectWithValue: ctlVal, origin, ctlNum, test and Check 3. Wait until control object returns to the “unselected state”, client requests either GetDataValues(stSeld) or SelectWithValue or Operate 4. Repeat step 1-3 for the other attributes in step 2 | | |
| Comment | | |