Solution to redmine 652

 Publisher can use maximum number of dataset elements

October 18, 2022

Some interpretation of maxAttributes is ambiguous. Clarified to mean ds members regardless of FCD or FCDA. See also <https://iec61850.tissue-db.com/tissue/719>. ICTs and servers found to enforce wrong rule.

Solution: add a new mandatory test case sGop13

|  |  |  |
| --- | --- | --- |
| **sGop13** | **Max number of dataset elements** | [ ]  Passed[ ]  Failed[ ]  Inconclusive |
| IEC 61850-7-2 Subclause 22.2IEC 61850-8-1 Subclause 18.1SCL Services ConfDataSet maxAttibutes |
| Expected result1. DUT sends GOOSE messages with numdatsetEntries >= SCL Services ConfDataSet maxAttibutes |
| Test descriptionConfigure DUT with GoCB with a dataset with at least maxAttibutes number of FCD dataset elements1. DUT sends GOOSE messages  |
| CommentFCD data set elements have no daName |

Update table A.4.2 and certificate template and add sGop13 as mandatory.