Solution to redmine 5961

sCtl16 add LocSta to match table B.1

October 19, 2022

Comment Thierry:

1) If LocSta is not present then the device does not make a difference between remote and station operation. LocSta has been introduced to enhance the switching hierarchy by differentiating operations originated in the station from operations originated in the control center.

2) There is no default value for LocSta - if it is not present, operation from station and remote are treated the same - with regard to the Loc switching hierarchy.

3) Ct29 is needed, because usage of 1 (bay-control), 4 (automatic-bay) can be verified and limited by the implementaton: Local HMI (1) is done locally not over communication, Automatic bay (4) - Logic is done locally not over communication.

When XCBR/XSWI.Loc is true, then even CSWI can not operate the switching equipment. Since sCtl16 is using CSWI for switching operation, then sCtl16 can only be performed with XCBR/XSWI.Loc = false

Richard:


Some devices have LocSta others don’t. We better clarify that if LocSta is present it shall be F, so at SBOes step 3 with orCat=3 the SelectWithValue shall succeed.

Clarify change “DUT to Local” as follows: CSWI/XCBR/XSWI.Loc=True

Move "if supported" from test description to requirement condition table A4.2

PIXIT; we keep Ct29 as is

|  |  |  |  |
| --- | --- | --- | --- |
| Ct29 | Amd1 | Does the IED support XCBR/XSWI.Loc=False and LLN0/CSWI.Loc=True  When yes, does the IED accept the control when orCat=1 or 4 Local | DOns: Y/N, orCat 1-4: Y/N  SBOns: Y/N, orCat 1-4: Y/N  DOes: Y/N, orCat 1-4: Y/N  SBOes: Y/N, orCat 1-4: Y/N |



For the last steps XCBR/XSWI.Loc=False while CSWI.Loc=T; orCat Bay = allowed.

Table A.4.2; update condition to CSWI.Loc. XCBR/XSWI.Loc is mandatory

| 12: Control general | sCtl5, sCtl8, sCtl9, sCtl10, sCtl11, sCtl25 | SCL-Operate time reasonably large: sCtl14  PIXIT-Sr5 Behaviour=off: sCtl15  SCL-CSWI.Loc: sCtl16  SCL-LocSta: sCtl17 |
| --- | --- | --- |

Updated sCtl16:

|  |  |  |
| --- | --- | --- |
| **sCtl16** | **Control an object when the IED is in Local operation** | Passed  Failed  Inconclusive |
| IEC 61850-7-2 Subclause 20.5.2.6, Table 54  IEC 61850-7-4 Table B.1  IEC 61850-8-1 Subclause 20.6, 20.7 and 20.8  PIXIT: Ct13, Ct20, Ct21, Ct29 | | |
| Expected result  a)   DOns        1,3   DUT sends Operate response- with optional AddCause “Blocked-by-switching-hierarchy” or “Not-supported”        2.    DUT behaves according to the PIXIT  b)   SBOns        1,7.  DUT sends Select response- or Operate response- with optional AddCause “Blocked-by-switching-  hierarchy” or “Not-supported”        3.    DUT sends Select response+        5.    DUT sends Operate response- with optional AddCause “Blocked-by-switching-hierarchy” or               “Object-not-selected”        6.     DUT behaves according to the PIXIT  c)   DOes        1,3.  DUT sends Operate response- with AddCause “Blocked-by-switching-hierarchy” or “Not-supported”        2.    DUT behaves according to the PIXIT  d)   SBOes        1,7.  DUT sends SelectWithValue or Operate response- with AddCause “Blocked-by-switching-  hierarchy” or “Not-supported”        3.    DUT sends SelectWithValue response+        5.    DUT sends Operate response- with AddCause “Blocked-by-switching-hierarchy”  or              “Object-not-selected”        6.    DUT behaves according to the PIXIT | | |
| Test description  Test engineer changes the DUT to “Local”; CSWI.Loc=True and XCBR/XSWI.Loc=True and LocSta=False if supported     1. DOns   1.   Client sends Operate request with following values of orCat = 1, 2, 3, 4, 5, 6  When supported change XCBR/XSWI.Loc from True to False, keep LLN0/CSWI.Loc=True and perform steps 2,3  2.   The matching client sends Operate request with orCat = 1, 4  3.   The matching client sends Operate request with orCat = 2, 3, 5, 6   1. SBOns 2. Client sends Select request, on respond+ Client sends Operate with following values of orCat = 1, repeat for orCat = 2, 3, 4, 5, 6 3. Test engineer changes CSWI/XCBR/XSWI.Loc=False 4. Client sends Select request 5. Test engineer changes CSWI/XCBR/XSWI.Loc=True 6. Client sends Operate request with orCat=3 within the select timeout   When supported change XCBR/XSWI.Loc from True to False, keep CSWI.Loc=True and perform steps 6,7   1. Repeat step 1 with orCat = 1, 4 with a matching client 2. Repeat step 1 with orCat = 2, 3, 5, 6 with a matching client 3. DOes   1.   Client sends Operate request with following values of orCat = 1, 2, 3, 4, 5, 6  When supported change XCBR/XSWI.Loc from True to False, keep CSWI.Loc=True and perform steps 2,3  2.   The matching client sends Operate request with orCat = 1, 4  3.   The matching client sends Operate request with orCat = 2, 3, 5, 6   1. SBOes 2. Client sends SelectWithValue request, on respond+ Client sends Operate with orCat=1, repeat for orCat = 2,3,4,5,6 3. Test engineer changes CSWI/XCBR/XSWI.Loc=False 4. Client sends SelectWithValue request with orCat=3 5. Test engineer changes CSWI/XCBR/XSWI.Loc=True 6. Client sends Operate request with orCat=3 within the select timeout   When supported change XCBR/XSWI.Loc from True to False, keep CSWI.Loc=True and perform steps 6,7   1. Repeat step 1 with orCat = 1, 4 with a matching client   7. Repeat step 1 with orCat = 2, 3, 5, 6 with a matching client | | |
| Comment   Note: “matching” client means a client that is allowed by the server to issue control | | |