Solution to redmine 6188

**sSBOns8 does not consider PIXIT Ct13**

November 29, 2022

Remove the orCat=1 check from sSBOns8

Compare the tracked changes (removed the original step 2.c.)

|  |  |  |
| --- | --- | --- |
| **sSBOns8** | **Verify cancel parameters are ignored for SBOns** | [ ]  Passed[ ]  Failed[ ]  Inconclusive |
| IEC 61850-7-2 Subclause 20.2.2IEC 61850-8-1 Subclause 20.4 and 20.7TISSUE 1703 |
| Expected result1. DUT responds with Select.response+ 2. DUT responds with Cancel.response+ 3. DUT indicates selection is canceled4. The control object returns to the “Unselected” state: stSeld=F or Select response+  |
| Test description1. Client sends valid Select request to a control object2. Client sends Cancel with same ControlObjectReference as the Select and one of the following attribute values:1. ctlVal = present value
2. ctlVal = value different from present value
3. origin.orIdent = all zeroes
4. ctlNum = 0
5. T = present time - 1 minute
6. T = present time + 1 minute
7. Test = true
8. Check = 00
9. Check = 11
10. To verify the Unselected/Ready state client requests either GetDataValues(stSeld) or Select after each step followed by a cancel
11. Repeat steps 1-3 for each item in step 2
 |
| Comment |