Solution to redmine 6188

**sSBOns8 does not consider PIXIT Ct13**

November 29, 2022

Remove the orCat=1 check from sSBOns8

Compare the tracked changes (removed the original step 2.c.)

|  |  |  |
| --- | --- | --- |
| **sSBOns8** | **Verify cancel parameters are ignored for SBOns** | Passed  Failed  Inconclusive |
| IEC 61850-7-2 Subclause 20.2.2  IEC 61850-8-1 Subclause 20.4 and 20.7  TISSUE 1703 | | |
| Expected result  1. DUT responds with Select.response+  2. DUT responds with Cancel.response+  3. DUT indicates selection is canceled  4. The control object returns to the “Unselected” state: stSeld=F or Select response+ | | |
| Test description  1. Client sends valid Select request to a control object  2. Client sends Cancel with same ControlObjectReference as the Select and one of the following attribute values:   1. ctlVal = present value 2. ctlVal = value different from present value 3. origin.orIdent = all zeroes 4. ctlNum = 0 5. T = present time - 1 minute 6. T = present time + 1 minute 7. Test = true 8. Check = 00 9. Check = 11 10. To verify the Unselected/Ready state client requests either GetDataValues(stSeld) or Select after each step followed by a cancel 11. Repeat steps 1-3 for each item in step 2 | | |
| Comment | | |