## Slide 1: VSR – Variable Shunt Reactor Modeling

## Slide 2: VSR Capacitor Banks

## Slide 3: Variable Shunt Reactor
VSR is a Shunt Reactor with tap changer (same type used in power transformers)
Range is from 20% to 100% of maximal susceptance
It cannot have tap changer at 0 (a special breaker is assigned to deenergize VSR)

## Slide 4: Resistance, Reactance per tap position - linear
Chart: R, X
| 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
R | 0.52658 | 0.55332 | 0.57866 | 0.60393 | 0.62919 | 0.65446 | 0.67977 | 0.70503 | 0.73038 | 0.75568 | 0.78882 | 0.82197 | 0.85516 | 0.88834 | 0.90245 | 0.9293 | 0.95464 | 0.9799 | 1.0051 | 1.0304 | 1.0557 | 1.081 | 1.1063 | 1.1316 | 1.1648 | 1.1979 | 1.2311 | 1.2642 | 1.2974
X | 2363.7 | 2308.2 | 2253.4 | 2199.9 | 2146.4 | 2094.2 | 2048.6 | 2003.3 | 1959.2 | 1915.4 | 1872.2 | 1829.8 | 1788.6 | 1747 | 1707.9 | 1672 | 1626.2 | 1582.7 | 1539.1 | 1496.1 | 1457.3 | 1420.6 | 1384.1 | 1348.5 | 1314 | 1279.7 | 1245 | 1212.2 | 1180.4
R measured using small DC current through each coil Z measured using small AC current through each coil

## Slide 5: 1/Z=1/(R+jX)=G+jB=Y Admittance usually used for shunt model (I=YU)
Chart: G, B
| 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1
R | 9.4251e-08 | 1.0385e-07 | 1.1396e-07 | 1.2479e-07 | 1.3657e-07 | 1.4923e-07 | 1.6198e-07 | 1.7568e-07 | 1.9028e-07 | 2.0598e-07 | 2.2505e-07 | 2.455e-07 | 2.6731e-07 | 2.9107e-07 | 3.0939e-07 | 3.3242e-07 | 3.6099e-07 | 3.9119e-07 | 4.2432e-07 | 4.6036e-07 | 4.971e-07 | 5.3564e-07 | 5.7749e-07 | 6.2229e-07 | 6.746e-07 | 7.3148e-07 | 7.9427e-07 | 8.6034e-07 | 9.3113e-07
X | -0.00042307 | -0.00043324 | -0.00044377 | -0.00045457 | -0.0004659 | -0.00047751 | -0.00048814 | -0.00049918 | -0.00051041 | -0.00052208 | -0.00053413 | -0.00054651 | -0.0005591 | -0.00057241 | -0.00058551 | -0.00059809 | -0.00061493 | -0.00063183 | -0.00064973 | -0.0006684 | -0.0006862 | -0.00070393 | -0.00072249 | -0.00074156 | -0.00076103 | -0.00078143 | -0.00080321 | -0.00082495 | -0.00084717

## Slide 6: Capacitor Banks

## Slide 7: Capacitor Banks
A grouping of several capacitors
Sections start at 0 (goes from 0 to 100%)
Sections often equal (each section same G and B)

## Slide 8: VSR Capacitor banks
Shunt reactor with tap changer
Usually linear for R, X
Starts at 1
First tap different value than difference between other taps
First tap can have maximum or minimum admittance
A grouping of capacitors
Usually linear for G, B
Starts at 0, 0 is implied
All sections equal usually
Each section adds more G and B

## Slide 9: Current ShuntCompensator model suited for capacitor banks not for VSR

## Slide 10: VSR as NonlinearShuntCompensator
Some vendors have implicit 0 sections (with G=0 and B=0)
  Power flow calculations allow a choice of 0 section which VSR cannot execute
  Optimal Power flow can suggest 0 sections
  Voltage regulation simulation use 0 section

## Slide 11: VSR as a specialization of NonlinearShuntCompensator
Note for VariableShuntCompensator would say: Variable shunt compensator sectionNumbers start at 1. 0 sectionNumber is not allowed.

## Slide 12: LinearVariableShuntCompensator
To model the linearity of VSR a R and X need to be used
This has no use for calculations because modeling of shunts use admittance (G+jB) – calculations would not see linearity
Recommend not to use linear model of VSR

## Slide 13: Automatic regulation – no need to change

## Slide 14: OPF calculations
two tier optimization
optimization in the range using taps (20%-100%)
  to be used for real-time operation
optimization of energized status
  for optimization of the several hours (days) ahead

## Slide 15: Roadmap
To be a part of revisiting of SVC/STATCOM and looking into capacitor banks
Coordinate with Asset and AssetInfo
Topic for CIM 18

## Slide 16: NonlinearShuntCompensatorPoint Note spelling error
A non linear shunt compensator bank or section admittance value. The number of NonlinearShuntCompensatorPoint instances associated with a NonlinearShuntCompensator shall be equal to ShuntCompensator.maximumSections. ShuntCompensator.sections shall only be set to one of the NonlinearShuntCompensatorPoint.sectionNumber. There is no interpolation between NonlinearShuntCompensatorPoint-s.