## Slide 1: Change tracking in SCL
Th. Dufaure, C. Bloch, P. Martin, Ch. Brunner, Ch. Frei, W. Wimmer
V4
2017-01

## Slide 2: Use case : SCT uses intended IxD file? ICT uses intended SCD file?
Original purpose
  ICT / IED engineer checks that SCT / system engineer used the intended IxD for system engineering
Final purpose
  IED has intended configuration

## Slide 3: Use case 1: implementation
IED configuration from ICT is identified by
  NamPlt.configVersion, .paramRev, .valRev
  Usable online as well as between SCT/ICT
  Draw back: Is defined per LD, i.e. all LDs need to be checked
Proposed solution
  LPHD contains RevPlt:LPL containing IED level configVersion / paramRev / valRev

## Slide 4: Information flow
ICT
SCT
IxD
Header.version = IV1 (if IR1 was IID, else IV2)
Header.Revision = IR2
IED.LPHD.configRev= I2
IED.LPHD.paramRev = 3
IED.LPHD.valRev = 2
Header.version = SV1
Header.Revision = SR1
IED.LPHD.configRev= I1
IED.LPHD.paramRev = 2
IED.LPHD.valRev = 1
Header.version = CI1
Header.Revision = CI1
IED.LPHD.configRev= I2
IED.LPHD.paramRev = 3
IED.LPHD.valRev = 2
IID
SCD
SCD
1
2
4
3
5
6
8
7
Header.version = SV1
Header.Revision = SR2
IED.LPHD.configRev= I2
IED.LPHD.paramRev = 3
IED.LPHD.valRev = 2
IED
ICT
Header.version = IV1
Header.Revision = IR1
IED.LPHD.configRev= I1
IED.LPHD.paramRev = 1
IED.LPHD.valRev = 1
CID
9

## Slide 5: Note regarding LLN0.paramRev, valRev
paramRev and valRev allow a granularity at logical device or logical node
Online configuration changes are possible
Offline changes by an increment of 10 000, while online changes are indicated by an increment of 1

## Slide 6: Parallel work
SCT
IID
Header.version = IV3
Header.revision = IR3
IED.LLN0.configRev= I3
IED.LLN0.paramRev = 30 000
IED.LLN0.valRev = 20 000
Header.version = SV1
Header.revision = SR1
IED.LLN0.configRev= I1
IED.LLN0.paramRev = 20 000
IED.LLN0.valRev = 10 000
SCD
1
2
4
3
5
ICT
Header.version = IV1
Header.revision = IR1
IED.LLN0.configRev= I1
IED.LLN0.paramRev = 10 000
IED.LLN0.valRev = 10 000
Header.version = IV2
Header.revision = IR2
IED.LLN0.configRev= I2
IED.LLN0.paramRev = 20 000
IED.LLN0.valRev = 20 000
3
20 000≠20 000
There is no configRev, paramRev, valRev in DPL.
Extension of DPL with configRev, paramRev and valRev does not help, as in the example illustrated 20000!=20000 independently on LN used.

## Slide 7: Parallel work - Proposal
SCT
IID
Header.version = IV3
Header.revision = IR3
IED.SCDVersion = SV1.SR1
IED.LLN0.paramRev = 30000
IED.LLN0.valRev = 20000
Header.version = SV1
Header.revision = SR1
IED.minSCDVersion = SV1.SR1
IED.IIDVersion = IV1.IR1
IED.LLN0.paramRev = 20000
IED.LLN0.valRev = 10000
SCD
1
2
4
3
6
ICT
Header.version = IV1
Header.revision = IR1
IED.SCDVersion = 0
IED.LLN0.paramRev = 10000
IED.LLN0.valRev = 10000
Header.version = IV2
Header.revision = IR2
IED.SCDVersion = 0
IED.LLN0.paramRev = 20000
IED.LLN0.valRev = 20000
3
IED.SCDVersion:
last Version of the SCD that ICT has imported. Initialized with 0
IED.minSCDVersion:
version of the SCD that contains the latest modifications related to the IED
IED.IIDVersion: last IID Version that has been imported by SCT
5
Users resolves
conflicts

## Slide 8: Parallel work - Proposal
Add SCL attributes
  IED.IIDversion, IED.IIDrevision
    Updated by SCT only
    Indicates latest ICD/IID Version / Revision imported by SCT
-> SCT can easily verify if latest IID version is used in the station file
-> ICT can easily verify if latest IID version was used by the SCT

## Slide 9: Parallel work - Proposal
Add SCL attributes
  IED.minSCDversion, minSCDrevision
    Set by the SCT only as soon as a modification for a given IED needs to be processed by the ICT
    Version / Revision of the SCD that contains the last modifications related to the IED

## Slide 10: Parallel work - Proposal
Add SCL attributes
  IED.SCDversion, IED.SCDrevision
    Updated by ICT only
    Indicates latest SCD Version / Revision imported by ICT
-> SCT can easily indicates that the ICT has to be updated with the minSCDversion / revision
-> ICT can easily verify if latest SCD version contains modifications of relevant for the device configuration

## Slide 11: Parallel work - Proposal
Extend DPL CDC
  scdVersion, scdRevision, iidVersion, iidRevision
    Updated by ICT only
    Indicates at physical device level latest SCD Version / Revision imported by ICT
    Indicates IID Version / Revision used by ICT when created CID
-> Online tool can easily verify if latest versions were used for device configuration (System Management, Integrity of configurations)
*a physical device usually contain several hierarchically organized LDevice. A single SCL file is used for the configuration purpose, therefore a single location is sufficient. An analysis involving paramRev, valueRev is powerfull to locate the online modifications.
*