## Slide 1: CIM models for capabilities of Grid Edge Devices and EV as DERs Discussion with reference to IEEE 1547, IEC 61850-7-420, IEC 61968-5
Tom Berry
Event: UCA TF13 29 January 2025
Updated: CIM UML Features 13 February 2025
Location: Remote

## Slide 2: DER capabilities and controls: principles
Assets, AssetInfo – used to initialize Grid, Market resource models
  Implies similar, maybe identical classes associated to Asset or PowerSystemResource
Market:RegisteredDistributedResource is equivalent to
Grid :{PowerElectronicsConnection + n*PowerElectronicsUnit}
Grid resource modelling can re-use RegisteredResource aggregation
IEC 62746-4 models partially supersede DERGroup from IEC 61968-5
Resource associations with Measurements and Meters are a way to record mappings to the real-time communication systems & protocols
Other mappings like IEC 61850 and IEEE 2030.5 may need new classes

## Slide 3
Reminder – these are different resources

## Slide 4: Control parameters
working proposal based on IEEE 1547
To be mapped to IEC 61850
Power limits should be upper and lower limits
To add settings to show
gridFormingCapability / Mode
How to handle regional specific rules for grid forming ?
Maybe different settings for blackStartCapability / Mode
Similar, maybe identical, classes can be used for assets and for resources

## Slide 5: Regardless of assets …
Grid and Market views could / should share same model of control capabilities

## Slide 6: Grid: Capabilities & Control Functions
Wires class have nameplate parameters
Function Blocks provide a richer set of functions than Regulating Control
Function blocks can also be defined to apply operational limits to P,Q
Updated 13/02

## Slide 7: Grid – Market: explicit association for resources
Grid resource could correspond to either
- aggregated resource
- physical resource
Update
resources may be controllable loads
=> association with Energy Connection
Updated 13/02

## Slide 8: Real-time communication #1 IEC 61850 mapping
New classes and associations to support mapping to IEC 61850 communication (mainly identification).
Updated 13/02

## Slide 9: Real-time communication #1 SCADA Package name / description
SCADA is the package name, not a system, which is confusing.
Redmine 7124
Maybe change package name
Maybe change description to:
Contains entities to model information used for operational supervision, control, and data acquisition in power system applications function.
Supervision involves real-time monitoring and decision support, enabling operator and automated control of equipment such as opening or closing a breaker. Data acquisition gathers real-time measurements from various sources, independent of the underlying communication technology.
Updated 13/02

## Slide 10: Real-time communication #2 Generic interface
Power management functions are “pure” calculation for supporting analyses
Add more function blocks for links to the outside world
Note: this means models also need function-function links
skip

## Slide 11: IEC 62746-4 models partially supersede DERGroup from IEC 61968-5
Classes in yellow have an equivalent in IEC 62746-4
Classes in orange have no existing direct mapping
DERFunctions – capabilities
DERMonitorableParameter – a way of exchanging measurements and setpoints.
DERGroupDispatch = ???
EndDeviceGroup = a specific type of aggregation

## Slide 12: Measurement, MeterReading, MonitorableParameter
= alternative ways of collecting data
Needs more thought and discussion …

## Slide 13: DERFunction and MonitorableParameter
Proposal:
Link EndDeviceGroup to virtual resource that has the function parameters.
And may or may not be associated with a registered resource
Updated 13/02

## Slide 14: DERFunction and MonitorableParameter
BUT
Two ways of defining groups
Updated 13/02

## Slide 15: To do
Support for IEEE 2030.5
Support for changing DER parameters by schedules
…