Abstract

* sSvs16 Verify that the DUT process sampled values with quality test is true when the device is in test, and ignores such values when device is not in test

|  |  |  |
| --- | --- | --- |
| **sSvs16** | **Verify that the DUT process sampled values with quality test is true when the device is in test, and ignores such values when device is not in test** | **[ ]  Passed****[ ]  Failed****[ ]  Inconclusive** |
| IEC 61850-7-4 Annex APIXIT Sr5, Svs1a |
| Expected result2. and 5. DUT ignores the samples flagged with quality test trueOther steps. DUT processes the samples according to PIXIT |
| Test descriptionForce DUT into Mode = on 1. SIMULATOR publishes SV stream with samples flagged quality test false2. SIMULATOR publishes SV stream with samples flagged quality test true3. SIMULATOR publishes SV stream with samples flagged quality test falseForce DUT into Mode = blocked (when supported)4. SIMULATOR publishes SV stream with samples flagged quality test false5. SIMULATOR publishes SV stream with samples flagged quality test true6. SIMULATOR publishes SV stream with samples flagged quality test falseForce DUT into Mode = test (when supported)7. SIMULATOR publishes SV stream with samples flagged quality test false8. SIMULATOR publishes SV stream with samples flagged quality test true9. SIMULATOR publishes SV stream with samples flagged quality test falseForce DUT into Mode = test/blocked (when supported)10. SIMULATOR publishes SV stream with samples flagged quality test false11. SIMULATOR publishes SV stream with samples flagged quality test true12. SIMULATOR publishes SV stream with samples flagged quality test false |
| Comment |

Add to certificate as mandatory

Add to table A4.2 as mandatory

Abstract

* sGos23 Verify that the DUT process GOOSE data values with quality test is true when the device is in test, and ignores such values when device is not in test

|  |  |  |
| --- | --- | --- |
| **sGos23** | **Verify that the DUT process GOOSE data values with quality test is true when the device is in test, and ignores such values when device is not in test** | **[ ]  Passed****[ ]  Failed****[ ]  Inconclusive** |
| IEC 61850-7-4 Annex APIXIT Sr5 |
| Expected result2. and 5. DUT ignores the data value changes flagged with quality test true (and does not send GOOSE with the changed values)Other steps. DUT updates the value and sends a GOOSE message with the changed value |
| Test descriptionTest engineer configures the DUT with subscribed GOOSE with FCDA (ping-pong mechanism) Force the subscriber Logical Node into Beh = on 1. SIMULATOR publishes GOOSE message with changed data values flagged quality test false2. SIMULATOR publishes GOOSE message with changed data values flagged quality test true3. SIMULATOR publishes GOOSE message with changed data values flagged quality test falseForce the subscriber Logical Node into Beh = blocked (when supported)4. SIMULATOR publishes GOOSE message with changed data values flagged quality test false5. SIMULATOR publishes GOOSE message with changed data values flagged quality test true6. SIMULATOR publishes GOOSE message with changed data values flagged quality test falseForce the subscriber Logical Node into Beh = test (when supported)7. SIMULATOR publishes GOOSE message with changed data values flagged quality test false8. SIMULATOR publishes GOOSE message with changed data values flagged quality test true9. SIMULATOR publishes GOOSE message with changed data values flagged quality test falseForce the subscriber Logical Node into Beh = test/blocked (when supported)10. SIMULATOR publishes GOOSE message with changed data values flagged quality test false11. SIMULATOR publishes GOOSE message with changed data values flagged quality test true12. SIMULATOR publishes GOOSE message with changed data values flagged quality test false. |
| Comment |

Add to certificate as mandatory

Add to table A4.2 as mandatory